## Slide 1
Maintenance
Iverson

## Slide 2
CONTENT
Fuse
01
IGBT
02
Soft Start Resistor
03

## Slide 3
Fuse Testing
Iverson

## Slide 4
S Fuse Testing-AHF
Equipment: electricity Multimeter
Setting: Resistor Band
Good: the resistor value is close to 0
Fault: the resistor value is close to infinity
Iverson

## Slide 5
S Fuse Testing-AHF
Iverson
Notes: 铜柱：copper cylinder
铜排：basbur

## Slide 6
S Fuse Testing-AHF
Iverson

## Slide 7
S Fuse Testing-AHF
Iverson

## Slide 8
S Fuse Testing-AHF
Equipment: electricity Multimeter
Setting: Resistor Band
Good: the resistor value is close to 0
Fault: the resistor value is close to infinity
Iverson

## Slide 9
IGBT Testing
Iverson

## Slide 10
S IGBT Testing-Three Types
Socket Type IGBT
Iverson

## Slide 11
Socket Type IGBT
IGBT Testing point is for diode
Four Testing point
From 3 to 5 ;
From 5 to 1;
Useful : Both Two diode means voltage is about 0.66V
From 6 to 2 ;
From 2 to 4 ;
Useful : Both Only one diode, means voltage is about 0.33V
S IGBT Testing-Three Types
Iverson

## Slide 12
Socket Type IGBT
S IGBT Testing-Three Types
Iverson

## Slide 13
Testing point (From 5 to 1)-0.66V
S IGBT Testing-Three Types-Socket Type IGBT
Iverson

## Slide 14
Testing point (From 3 to 5)-0.66V
S IGBT Testing-Three Types-Socket Type IGBT
Iverson

## Slide 15
4 and 6 Testing Point
S IGBT Testing-Two Types-Socket Type IGBT
Iverson

## Slide 16
Testing point (From 6 to 2)-0.33V
S IGBT Testing-Three Types-Socket Type IGBT
Iverson

## Slide 17
Testing point (From 4 to 2)-0.33V
S IGBT Testing-Three Types-Socket Type IGBT
Iverson

## Slide 18
S IGBT Testing-Three Types-For Plug One
Iverson

## Slide 19
S IGBT Testing-Three Types-For Plug One
Iverson

## Slide 20
S IGBT Testing-Three Types-For Plug One
Iverson
Testing Point: “EH1” – “+BUS”
“N” – “EH1”
“(AC)EH2”—EH1
“-BUS” –”EB1”
“EB1” – “N”
“EB1” –”AC”

## Slide 21
S IGBT Testing-Three Types
- /
6 Testing Points
“–” to “ 3 “ - 0.33V
“ 3 ” to “ 2 ” - 0.33V
“ 2 “ to “ 1” - 0.33V
“ 1 “ to “ - ” - 0.33V
“ 3 ” to “ N ” - 0.33V
“ N ” to “ 1 ” - 0.33V
Integrate Type IGBT
Iverson

## Slide 22
Integrate Type IGBT
S IGBT Testing-Three Types-integrate Type IGBT
Iverson

## Slide 23
Testing point (From — to 3)-0.33V
S IGBT Testing-Three Types-integrate Type IGBT
Iverson

## Slide 24
Testing point (From 3 to 2)-0.33V
S IGBT Testing-Three Types-integrate Type IGBT
Iverson

## Slide 25
Testing point (From 2 to 1)-0.33V
S IGBT Testing-Three Types-integrate Type IGBT
Iverson

## Slide 26
Testing point (From 3 to N )-0.33V
S IGBT Testing-Three Types-integrate Type IGBT
Iverson

## Slide 27
Testing point (From N to 1)-0.33V
S IGBT Testing-Three Types-integrate Type IGBT
Iverson

## Slide 28
Soft Start Resistor
Iverson

## Slide 29
S Soft Start Resistor Testing-AHF-Function normally
Iverson

## Slide 30
S Soft Start Resistor Testing-AHF-Function normally
Iverson

## Slide 31
S Soft Start Resistor Testing-AHF-Function normally
Iverson

## Slide 32
S Soft Start Resistor Testing-AHF-Notice
Notice
1、Only two phase have soft start resistor
2、With the soft start resistor, and if the multimeter shows infinity, means soft start resistor broken.
3、because the relay is parallel with the soft start resistor, and if the multimeter shows 0L, and it means the relay fault.
(Normal condition: Relay is off)
Iverson