## Slide 1
Items | 200V |  |  | 
 | Sinexcel AHF025/035 | Sinexcel AHF050/060 | Sinexcel AHF075/100 | Sinexcel AHF 150
System parameters |  |  |  | 
Rated input | 220V(-20% ～+20%) |  |  | 
Power grid frequence | 50/60HZ（range: 45Hz～62Hz） |  |  | 
Paraller quantities | Unlimited |  |  | 
Efficiency | ≥97% |  |  | 
Power grid structure | 3P3W/3P4W |  |  | 
Performance indicators |  |  |  | 
Control algorithm | FFT, intelligent FFT, instantaneous reactive power |  |  | 
Reaction time | <50μs |  |  | 
Overall response Time | <5ms |  |  | 
Target power factor | Adjustable from -1 to +1 |  |  | 
Switching frequency | average 20kHz, maximum 35kHz |  |  | 
Cooling air requirement | 321CFM | 321CFM | 543CFM | 825CFM
Noise level | <56dB |  |  | <65dB
Communications ports | RS485,and Ether net port(RJ45) |  |  | 
Communications protocols | MODBUS (RTU, TCP/IP) |  |  | 
Module display interface | 4.3-inch HMI(module), 7-inch HMI(central monitor), LED |  |  | 
Protection functions | Abnormal voltage/frequency protection; Inverter short-circuit protection; Abnormal output current protection; Inverter over-loaded protection, Over-tempearture protection etc,. |  |  | 
Mounting type | Wall-mounted/Rack-mounted/Cabinet |  |  | 
Dimensions (W x D x H) (mm³) | 400*490*150 (Rack-mounted) 440*150*470 (Wall-mounted) | 440*590*190 (Rack-mounted) 440*190*610 (Wall-mounted) | 500*600*190(75A) 440*599*230(100A) (Rack-mounted) 500*190*585(75A) 440*232*625(100A) (Wall-mounted) | 500*560*269 (Rack-mounted) 500*286*557 (Wall-mounted)
Net weight | 18kg | 35kg | 40kg | 48kg
Ambient temperature | ’-10℃～40℃ (derating if ambient temperature exceeds 45℃) |  |  | 
Relative humidity | 5% to 95%, non-condensing |  |  | 
protection class | IP20 (IP degrees can be customizd) |  |  | 
Qualifications | CE, cETLus, cULus |  |  | 
Standards Compliance | IEEE519, ER G5/4 , IEC 61000 |  |  | 
Specification of 200V Active Harmonic Filter