## Slide 2
“Main Interface”
“Main”:
Grid Current: after compensating
Load Current: before compensating
PF： power factor
RMS： root mean square
Power On： starting up
Power Off： shutdown
“Alarm”: system status (It includes the following three states).
“Stop”: stand by mode
“Alarm”: abnormal working condition
“Normal”: abnormal working condition

## Slide 3
“Data Interface”
This interface is about voltage/ frequency/THDu of AHF power access point, check 3-phase voltage waveform by clicking “waveform” , check each order of harmonic voltage distribution by clicking “Spectrum”
L1 corresponding to the A phase
L2 corresponding to the B phase
L3 corresponding to the C phase

## Slide 4
Voltage Waveform（L1/L2/L3）
Voltage Spectrum （L1/L2/L3）
“Waveform and Spectrum”

## Slide 5
“current”
Grid current ： the current after compensation
load current ：the current before compensation
Comp current ：the current outputted from AHF.
Check 3-phase current waveform by clicking “waveform” , check each order of harmonic current distribution by clicking “Spectrum”

## Slide 6
Grid current Spectrum（L1/L2/L3）
Waveform and Spectrum
Grid and load current Waveform（L1/L2/L3）

## Slide 7
Load current Waveform（L1/L2/L3）
Load current Spectrum（L1/L2/L3）
Waveform and Spectrum

## Slide 8
Compensation current Waveform（L1/L2/L3）
Compensation current Spectrum（L1/L2/L3）

## Slide 9
“Debugging”
Different setting values correspond to different internal variables of DSP. And it is forbidden to change from users.
Grid side / Load side (L1/L2/L3)
Apparent power,
Active power ,
Reactive power
cosΦ.
(Grid side means after compensation, Load side means before compensation.)
Debugging & Power Analysis

## Slide 10
Node1-3 are invalid,
It respectively AHF inner L1/L2/L3 the highest temperature. .
“ Version”
Software Version
Mxxx said monitoring software version information,
Dxxx of DSP software version information
“ IO & Temperature”

## Slide 11
advanced password : 654321
More parameters settings under the advanced password
System Parameter
(Basic parameters of the DSP control system)
Clear Fault
(After the AHF appeared some fault alarm, it need to click the "Clear fault" to restore normal work)
Monitor Parameter
(The basic parameters for monitor display)
Exit
(drop out From the parameter settings interface)
“Setting”

## Slide 12
System Parameter : Operation Mode:
Operation mode:
H（harmonic）: Harmonic compensation
Q (Reactive）: Reactive power compensation
B (Balancing) : unbalance compensation
Auto-ageing:
Manufacturer internal testing work mode, client shall be forbidden to use.
There have 12 kinds of operation modes
H H+B+Q Q+B+H
H+Q H+B B+H
H+Q+B Q+H B+H+Q
Auto-ageing Q+H+B B+Q+H
H+B+Q means harmonic compensation first, then compensating 3-phase unbalanced, finally compensating reactive power

## Slide 13
CT Location:
Supply Side
for single AHF system , supply side is mean the CT installed between Grid and AHF
Load Side
load side is mean the CT installed between AHF and loads, user can chose supply or load according to where is the CT installation point , for multiple AHFs system , use can only chose load side no matter CT installed on grid side or load side
Power ON Mode:
Auto : AHF can automatically start working when AHF power on
Manual: AHF will work when user clicking power on
Power ON Mode and CT Location

## Slide 14
Quantity:
Parameter a default value is 1, can not be changed
Total Capacity:
for single AHF system ，total capacity =AHF rate capacity , for multiple AHFs parallel system, total capacity=combining each single AHF rated capacity.
For example :
If AHF system capacity= 200A, AHF total capacity should be set as 200 for each 100A AHF
Quantity & Total Capacity:

## Slide 15
CT ratio:
The setting value need to correspond to the actual changes of external CT. The setting range: 150~30000. (500 means 500:5 .)
Constant Reactive:
Before setting this parameter need to consult the manufacturer engineers
Compensation mode:
Choose "Intelligent compensation" mode first. "sequential compensation" and "All compensation" are suitable for harmonic system that changes rapidly, and they are less stable than "Intelligent compensation".
Compensation mode & CT ratio

## Slide 16
Ext. Passive Filter:
Reserved.
CT Secondary Connect:
it is can only be set as series
Click “Page Down”
Inductor Current Configuration
In the auto-aging mode , choose inductance current or capacitive current output. And it is forbidden to change from users port.

## Slide 17
Click “Page Down”
(go to next page)
PT Ratio:
Equipment when being used get access to the grid through the transformer. And it is used to set the external transformer ratio. The default is 1.0 meaning 1∶1，ranging 0.1~25.
(Before the change must consult the Engineer)
Target Power Factor:
Adjusting the grid side power factor. (range: -1~1)

## Slide 18
“Page Down”
Controller Parameter I
Voltage loop control parameters, the larger parameters of the controller I is , the more stable voltage loop is . And it is forbidden to change from users.
Variable 1~6
Different setting values correspond to different internal variables of DSP . And it is forbidden to change by users.

## Slide 19
“Page Down”
Compensation Rate
Set the compensation ratio of compensation current measured by AHF. The setting range is 0~1, 1 on behalf of 100%.
Hybrid Parameters
Reserved (it is forbidden to change by users)

## Slide 20
Network Configuration & Module Capacity
Network Configuration
Set the network structure of AHF. It should be same as the actual network structure of system
it is forbidden to change by users.
Voltage Class:
set it same as what actual rate voltage of AHF
Module Capacity
Set the rated output current of the unit.
it is forbidden to change by users

## Slide 21
L1/ L2/ L3 Phase Angle Bias
Reserved. and can be changed by users
L1\L2\L3 Inductive Current Configuration:
Make the actual inductance current corresponds the
DSP value given by calibration.
it is forbidden to change by users
L1\L2\L3 CT current Configuration:
Make the load current that is sampled by the main control DSP corresponds to the actual load current by calibration
it is forbidden to change by users
Phase Angle Bias & current configuration

## Slide 22
L1\L2\L3 Input Voltage Configuration
Make the grid voltage value that is sampled by the main control DSP corresponds to the actual grid voltage by calibration.
it is forbidden to change by users
L1\L2\L3 Inverter Current Configuration
Make the actual current of the inverter corresponds to the DSP value given by calibration.
it is forbidden to change by users
current configuration & voltage configuration

## Slide 23
Input-Frequency Rank
Setting the input-frequency of equipment.
The value should correspond to actual system frequency.
Input Current Abnormal
AHF giving an alarm and stopping outputting current
when its input-current goes wrong under enabling mode.
In disabling mode ,it keeps outputting current.
PLL
Lock the phase angel of the grid and default enabling. And it is forbidden to change from users.
Input-frequency Rank & PLL & Input Current Abnormal

## Slide 24
DYN11/DYN12/YYN
The setting value should corresponding to actual connecting value of the external transformer which connected between AHF and grid.
it is forbidden to change by users
CT Correct Enable
Reserved and can not be change by users
DYN11/DYN12/YYN & CT Correct Enable

## Slide 25
Phase Angle Bias &Derating Coeff & Temperature Derating & Capacitive Reactive Enable
Phase Angle Bias
Adjusting the phase angel of compensation current to get more
accurate performance. it is forbidden to change by users
Derating Coeff
It is forbidden to change by users
Temperature Derating
The device will automatically reduce its current under
enable modewhen temperature reaches a certain value.
Capacitive Reactive Enable
when enabled the AHF can compensate both inductive and capacitive harmonic. When disabled the AHF will only provide inductive
Harmonic compensation

## Slide 26
“Page Down”
Grid Voltage Adjust
SVG might adjusting the voltage under enable mode.
Expiry Days
originally designed as a way of disabling the AHF after a certain
number of days operation
Out Current CT Ratio
The specific settings just for other large-capacity models.
LVRT
Low Voltage Ride Through. Has reversed functionality. When
enabled, if supply voltage drops below 90% for more than 2s then
AHF will stop. When disabled the AHF will work across its entire
voltage tolerance range.
Fan Gear
permits adjustment of cooling fan speed irrespective of AHF internal
temperature. 1.0 = 100% fan speed.

## Slide 27
Harmonic Comp. Setup interface
it is allow to adjust compensation rate of every order harmonics. The setting range: 0%~110%
Harmonic Comp. Setup

## Slide 28
Target Voltage
When the value exceeding the target voltage, AHF will go to adjust the voltage from other operation mode
Target Voltage

## Slide 29
Power Saving Function
Setting the time of power on and power off to achieve saving power.
Select Weekday
Setting the working days of the machine.
Select Holidays
Setting the time of start and end.
Power Saving Function

## Slide 30
“Monitor Parameter”
Local Address
Setting monitoring address
Time
Set current time.
Baud Rate
Setting the times of carriers that change in per unit time.
Language
Choose monitor display language.

## Slide 31
Active
Displays the current alarm information.
History
Display previous alarm information.
A total of 500 pieces of information can be recorded.
Download
Download recorded information by USB access
“Alarm”

## Slide 32
View the machine's operation record.
“Operations”